PILLAR FIRE HYDRANT  type NH1

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Pillar fire hydrant

* Made in accordance with the standard SRPS EN14384, type „A“

* Nominal sizes DN80, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* Wiht control valve

* Possibility of use even when the main valve seal is defective.

* Activation without additional tools.

* The possibility of blocking unauthorized use.

* Flow (za Di=2x50); Kv=min.140m3/h

* Activation moment: MOT=max.40Nm

* Repair of the main valve; the other hydrants remain in operation, without digging up the ground and without

dismalting the hydrant body.

* Outlets tilted toward the ground for 25˚

* Breakage due to force F; without damage to the pipeline, automatic stop of water discharage.

* Breaking moment M=max.6500Nm.

Flange EN1092-2

* Inlet connection:	(Du80, PN16) (Du100, PN16)

Particular request, „describe“

* Nominal height Hi:	         (1300) (1500) (1800)mm

Particular request, „specify“

* Outlets Di: 	                 (2x50+1x65)mm

* Outlet couplings:               (2xC+1xB) DIN, sistem „storz“

Specify label and standard

* Drainage system:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water:                        Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	               red

- underground part: black	                       special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

PILLAR FIRE HYDRANT type NH2

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Pillar fire hydrant

* Made in accordance with the satandard EN14384, type „A“

* Nominal sizes DN100, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* With control valve

* Possibility of use even when the main valve seal is defective

* Activation without additional tools

* The possibility of blocking unauthorized use

* Flow (za Di=2x65); Kv=min.270m3/h

* Activation moment: MOT=max.50Nm

* Repair of the main valve; the other hydrants remain in operation

* Outelts tilted toward the ground for 25˚

* Breakage due to force F; without damage to the pipeline, automatic stop of water discharage

* Breaking moment M=max.7800Nm

Flange  EN1092-2

* Inlet connction:	(Du100, PN16) (Du150, PN16)

Particular request, „describe“

* Nominal height Hi:	            (1350) (1550) (1850)mm

Particular request, „specify“

* Outlets Di: 	              (2x65+1x100)mm

* Outlets couplings:                (2xB+1xA) DIN, sistem „storz“

Specify label and standard

* Drainage system:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water:                Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	            red

- underground part: black

special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

PILLAR FIRE HYDRANT type NH3

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Pillar fire hydrant

* Made in accordance with the standard EN14384, type „A“

* Nominal sizes DN150, PN16

* Closing with the main vlave „from above“

* With isolation „pre-valve“, closing „from below“

* With control valve

* Possibility of use even when the main valve seal is defective

* Activation without additional tools

* The possibility of blocking unauthorized use

* Flow (za Di=2x100); Kv=min.520m3/h

* Activation moment: MOT=max.70Nm

* Repair of the main valve; the other hydrants remain in operation, without digging up the ground and

without dismalting the hydrant body

* Outlets tilted toward the ground for 25˚

* Beakage due to force F; without damage to the pipeline, automatic stop of water discharge

* Breaking moment M=max.14000Nm

Flange   EN1092-2

* Inlet connection:	(Du150, PN16)

Particular request, „describe“

* Nominal height Hi:	      (1350) (1550) (1850)mm

Particular request, „specify“

* Outlets Di:  	    (2x100+1x150)mm

* Outlet couplings:             Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

PILLAR FIRE HYDRANT WITH BREAK SYSTEM type LNH1

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Pillar fire hydarant with break system

* Made in accordance with the standard EN14384, type „C“

* Nominal sizes DN80, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* With control valve

* Activation without or with an additional tools

* The possibility of blocking unauthorized use

* Flow (za Di=2x50); Kv=min.145m3/h

* Activation moment: MOT=max.60Nm

* Repair of the main valve; the other hydarnts remain in operation, without digging up the ground and without

dismalting the hydrant

* Outlets tilted toward the ground for 25˚

* Breakage due to force F; no damage to the lower part of hydrant

* Breaking moment M=max.1200daN

Flange EN1092-2

* Inlet connection:	(Du80, PN16) (Du100, PN16)

Particular request, „describe“

* Visina do izlaznih otvora:	         (1300) (1500) (1800)mm

Particular request, „specify“

* Izlazni otvori Di: 	      (2x50+1x65)mm

* Izlazne spojnice:               (2xC+1xB) DIN, system „storz“

Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

PILLAR FIRE HYDRANT WITH BREAK SYSTEM  type LNH2

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Pillar fire hydarant with break system

* Made in accordance with the standard EN14384, type „C“

* Nominal size DN100, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* With control valve

* Activation without or with an additional tools

* The possibility of blocking unauthorized use

* Flow (za Di=2x65); Kv=min.270m3/h

* Activation moment: MOT=max.65Nm

* Repair of the main valve; the other hydarnts remain in operation, without digging up the ground and without

dismalting the hydrant

* Outlets tilted toward the ground for 25˚

* Breakage due to force F; no damage to the lower part of hydrant

* Breaking moment  M=max.1500daN

Flange  EN1092-2

* Inlet connection:	(Du100, PN16) (Du150, PN16)

Particular request, „describe“

* Visina do izlaznih otvora:	          (1350) (1550) (1850)mm

Particular request, „specify“

* Izlazni otvori Di:  	    (2x65+1x100)mm

* Izlazne spojnice:             (2xB+1xA) DIN, sistem „storz“

Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

MONITOR  type MNH1

PROCUREMENT DATA: *1

(See relevant prospect)

Hydrant:

* Name: Pillar fire hydrant

* Made in accordance with the standar EN14384, type „A“

* Nominal sizes DN80, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* Wiht control valve

* Possibility of use even when the main valve seal is defective.

* Activation without additional tools.

* The possibility of blocking unauthorized use.

* Flow (za Di=2x50); Kv=min.140m3/h

* Activation moment: MOT=max.40Nm

* Repair of the main valve; the other hydrants remain in operation, without digging up the ground and without

dismalting the hydrant body.

* Outlets tilted toward the ground for 25˚

* Breakage due to force F; without damage to the pipeline, automatic stop of water discharage.

* Breaking moment M=max.6500Nm

Flange EN1092-2

* Inlet connection:	     (Du80, PN16) (Du100, PN16)

Partiqular request, „describe“

* Nominal height Hi:	            (1300) (1500) (1800) mm

Particular request, „specify“

* Outlets Di: 	             (2x50+1x65)mm

* Outlet couplings:               (2xC+1xB) DIN, system „storz“

Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

Water launcher:

- nominal opening ................. Di = 65 mm

- nominla pressure ............... PN = 16 bar

- choice of jet shape

- choice of jet direction: both vertically or horizontally

- fixing the selected jet position

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs

MONITOR type MNH2

PROCUREMENT DATA: *1

(See relevant prospect)

Hydrant:

* Name: Pillar fire hydrant

* Made in accordance with the standar EN14384, type „A“

* Nominal size DN100, PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* Wiht control valve

* Possibility of use even when the main valve seal is defective.

* Activation without additional tools.

* The possibility of blocking unauthorized use.

* Flow (za Di=2x65); Kv=min.270m3/h

* Activation moment: MOT=max.50Nm

* Repair of the main valve; the other hydrants remain in operation, without digging up the ground and without

dismalting the hydrant body.

* Outlets tilted toward the ground for 25˚

* Breakage due to force F; without damage to the pipeline, automatic stop of water discharage.

* Breaking moment M=max.7800Nm

Flange EN1092-2

* Inlet connection	(Du100, PN16) (Du150, PN16)

Particular request, „describe“

* Nominal Height Hi:	      (1350) (1550) (1850)mm

Particular, „specify“

* Outlets  Di:   	     (2x65+1x100)mm

* Outlet couplings:           (2xB+1xA) DIN, system „storz“

Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

Water launcher:

- nominal openings ................. Di = (65) (100) mm

- nominal pressure ......................... PN = 16 bar

- choise of jet shape

- choice of jet direction: vertically/horizontally

- fixing the selected jet position

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs /     tecoopeng@mts.rs

UNDERGROUND FIRE HYDRANT type PH1

PROCUREMENT DATA: *1

(See relevant prospect)

* Name: Underground fire hydrant

* Made in accordance with the standard EN14389

* Nominal size (DN80;DN100), PN16

* Closing with the main valve „from above“

* With isolation „pre-valve“, closing „from below“

* Possibility of use even when the main valve seal is defective.

* Flow; Kv=min.105m3/h

* Activation moment: MOT=<40Nm

* Repair of the main valve; the other hydrants remain in operation, without digging up the ground and without

dismalting the hydrant body.

* Drainage system „all outside“; repair without dismalting the hydrant

Flange EN1092-2

* Inlet connection:	(Du80, PN16) (Du100, PN16)

Particular request, „describe“

* Nominal height Hi:	      (700) (850) (1000)mm

Particular request, „specify“

* Outlet Di: 	    65 mm

* Outlet couplings:             Specify label and standard

* Drainage sysem:

- all „outside“; repair without dismalting the hydrant body.

- water drain:

- type D1; immediately around the hydrant

- type D2; into the drainage basket, neto to the hydrant

* Medium: Water: 	Tehnical

Drinking

* Colors of external surface:

- aboveground part (without pipe):	       red

- underground part: black	               special request

* Warranty period: 5 years.

* Submit documents:

-„Prospect“;

-„Test Report“, issued by an „authorized body“;

-„Certificate of Conformity“, issued by an „authorized body“;

*1          If necessary „omit/add“

Srbija - 26000 PANČEVO, Savska 12 - 14.

Tel. +381 13 346226 Tel./Fax +381 13 346042

www.tecoop.co.rs / tecoopeng@mts.rs